## Fixture delta watts
Source: | http://www.sce.com/NR/rdonlyres/7A3455F0-A337-439B-9607-10A016D32D4B/0/spc_B_Std_Fixture_Watts.pdf
|  | Pre |  | Post
Lamp Size Removed |  | Pre Fixture Description | Watts/Fixture (PRE) | Pre Fixture Description | Watts/Fixture (POST) | Savings per lamp removed | Savings per lamp removed * Ballast Adj
8-ft T8 |  | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 109 | Fluorescent, (1) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 58 | 51 | 36.72
4-ft T8 |  | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 59 | Fluorescent, (1) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 31 | 28 | 20.16
3-ft T8 |  | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 46 | Fluorescent, (1) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 26 | 20 | 14.4
2-ft T8 |  | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 33 | Fluorescent, (1) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 20 | 13 | 9.36
8-ft T8 |  | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 167 | Fluorescent, (2) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 109 | 58 | 41.76
4-ft T8 |  | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 89 | Fluorescent, (2) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 59 | 30 | 21.6
3-ft T8 |  | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 67 | Fluorescent, (2) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 46 | 21 | 15.12
2-ft T8 |  | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 47 | Fluorescent, (2) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 33 | 14 | 10.08
8-ft T8 |  | Fluorescent, (4) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 219 | Fluorescent, (3) 96", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 167 | 52 | 37.44
4-ft T8 |  | Fluorescent, (4) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 112 | Fluorescent, (3) 48", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 89 | 23 | 16.56
3-ft T8 |  | Fluorescent, (4) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 87 | Fluorescent, (3) 36", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 67 | 20 | 14.4
2-ft T8 |  | Fluorescent, (4) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 61 | Fluorescent, (3) 24", T-8 lamp, Instant Start Ballast, NLO (BF: .85-.95) | 47 | 14 | 10.08
8-ft T8 |  | Fluorescent, (2) 96", ES lamp, MAG-STD | 128 | Fluorescent, (1) 96", ES lamp, MAG-STD | 75 |  | 53
4-ft T8 |  | Fluorescent, (2) 48", ES lamp, MAG-ES | 72 | Fluorescent, (1) 48", ES lamp, MAG-ES | 43 |  | 29
3-ft T8 |  | Fluorescent, (2) 36", ES lamp, MAG-STD | 73 | Fluorescent, (1) 36", ES lamp, MAG-STD | 42 |  | 31
2-ft T8 |  | Fluorescent, (2) 24", STD lamp | 56 | Fluorescent, (1) 24", STD lamp | 28 |  | 28
8-ft T8 |  | Fluorescent, (3) 96", ES lamp, MAG-STD | 203 | Fluorescent, (2) 96", ES lamp, MAG-STD | 128 |  | 75
4-ft T8 |  | Fluorescent, (3) 48", ES lamp, MAG-ES | 115 | Fluorescent, (2) 48", ES lamp, MAG-ES | 72 |  | 43
3-ft T8 |  | Fluorescent, (3) 36", ES lamp,MAG-STD | 115 | Fluorescent, (2) 36", ES lamp, MAG-STD | 73 |  | 42
2-ft T8 |  | Fluorescent, (3) 24", STD lamp | 62 | Fluorescent, (2) 24", STD lamp | 56 |  | 6
8-ft T8 |  | Fluorescent, (4) 96", ES lamp, MAG-STD | 256 | Fluorescent, (3) 96", ES lamp, MAG-STD | 203 |  | 53
4-ft T8 |  | Fluorescent, (4) 48", ES lamp, MAG-ES | 144 | Fluorescent, (3) 48", ES lamp, MAG-ES | 115 |  | 29
3-ft T8 |  | Fluorescent, (4) 36", STD lamp, MAG-STD | 162 | Fluorescent, (3) 36", ES lamp,MAG-STD | 115 |  | 47
2-ft T8 |  | Fluorescent, (4) 24", STD lamp | 112 | Fluorescent, (3) 24", STD lamp | 62 |  | 50

## Comparison
| Wattage of lamp removed | [9 empty] | Weighted average
| T8 |  |  |  |  | T12 |  |  |  |  | 80% T12, 20% T8
| Current Proposal | 2 to 1 | 3 to 2 | 4 to 3 | Average | Current Proposal | 2 to 1 | 3 to 2 | 4 to 3 | Average | Current Proposal | Using averages
8-ft T8 | 54.5 | 36.72 | 41.76 | 37.44 | 38.64 | 69 | 53 | 75 | 53 | 60.3333 | 66.1 | 55.9947
4-ft T8 | 29.5 | 20.16 | 21.6 | 16.56 | 19.44 | 40 | 29 | 43 | 29 | 33.6667 | 37.9 | 30.8213
3-ft T8 | 23 | 14.4 | 15.12 | 14.4 | 14.64 | 37 | 31 | 42 | 47 | 40 | 34.2 | 34.928
2-ft T8 | 16.5 | 9.36 | 10.08 | 10.08 | 9.84 | 25.5 | 28 | 6 | 50 | 28 | 23.7 | 24.368

## TRM Table
| Wattage of lamp removed |  | Weighted average
| T8 | T12 | 80% T12, 20% T8
8-ft T8 | 38.64 | 60.3333 | 55.9947
4-ft T8 | 19.44 | 33.6667 | 30.8213
3-ft T8 | 14.64 | 40 | 34.928
2-ft T8 | 9.84 | 28 | 24.368

## Average ballast impact
| 2 to 1 | 3 to 2 | 4 to 3 | Average | Average of all
T8 Instant Start Centium | 70.37% | 68.97% | 69.23% | 69.52% | 73.65%
T8 Instant Start Optaniur | 75.09% | 73.05% | 80.8% | 76.9%
T8 Programmed Start Parallel, Optaniur | - | 70.83% | 66.4% | 68.61%
HALCO |  |  |  |  | 72.22%
Universal |  |  |  |  | 71.61%
|  | Ballast Impact Factor used |  |  | 72%

## T8 Instant Centium
Source: | http://www.usa.lighting.philips.com/connect/tools_literature/additional-literature/electronic-fluorescent3.wpd
|  |  | Input power | Ballast Factor | BEF | Using Fixture Input power delta Methodology | Actual Delta | Actual as % of delta watts
1 lamp | F32T8 | 1 | 29 | 0.91 | 3.14
2 lamp | F32T8 | 1 | 37 | 1.05 | 2.84 | 27 | 19 | 70.37%
|  | 2 | 56 | 0.89 | 1.59
3 lamp | F32T8 | 2 | 65 | 1.01 | 1.55 | 29 | 20 | 68.97%
|  | 3 | 85 | 0.88 | 1.04
4 lamp | F32T8 | 3 | 93 | 1 | 1.08 | 26 | 18 | 69.23%
|  | 4 | 111 | 0.89 | 0.8

## T8 Instant Optaniur
Source: | http://www.usa.lighting.philips.com/connect/tools_literature/additional-literature/electronic-fluorescent3.wpd
|  |  | Input power | Ballast Factor | BEF | Using Fixture Input power delta Methodology | Actual Delta | Actual as % of delta watts
0.77 Ballast IOP
1 lamp | F32T8 | 1 | 25 | 0.77 | 3.08
2 lamp | F32T8 | 1 | 31 | 0.9 | 2.9 | 23 | 17 | 73.91%
|  | 2 | 48 | 0.77 | 1.6
3 lamp | F32T8 | 2 | 55 | 0.85 | 1.55 | 25 | 18 | 72%
|  | 3 | 73 | 0.77 | 1.05
4 lamp | F32T8 | 3 | Not provided |  |  | 21 | #VALUE! | #VALUE!
|  | 4 | 94 | 0.74 | 0.79
0.77 Ballast GOP
1 lamp | F32T8 | 1 | 26 | 0.77 | 2.96
2 lamp | F32T8 | 1 | 31 | 0.88 | 2.84 | 22 | 17 | 77.27%
|  | 2 | 48 | 0.78 | 1.63
3 lamp | F32T8 | 2 | 55 | 0.86 | 1.56 | 26 | 19 | 73.08%
|  | 3 | 74 | 0.77 | 1.04
4 lamp | F32T8 | 3 | 77 | 0.81 | 1.05 | 18 | 15 | 83.33%
|  | 4 | 92 | 0.78 | 0.85
0.88 Ballast IOP
1 lamp | F32T8 | 1 | 28 | 0.91 | 3.25
2 lamp | F32T8 | 1 | 35 | 1.05 | 3 | 27 | 20 | 74.07%
|  | 2 | 55 | 0.87 | 1.58
3 lamp | F32T8 | 2 | 63 | 1 | 1.59 | 27 | 19 | 70.37%
|  | 3 | 82 | 0.87 | 1.06
4 lamp | F32T8 | 3 | Not provided |  |  | 31 | #VALUE! | #VALUE!
|  | 4 | 113 | 0.88 | 0.78
0.88 Ballast GOP
1 lamp | F32T8 | 1 | 30 | 0.88 | 2.93
2 lamp | F32T8 | 1 | 34 | 1.03 | 3.03 | 24 | 20 | 83.33%
|  | 2 | 54 | 0.88 | 1.63
3 lamp | F32T8 | 2 | 59 | 1 | 1.68 | 30 | 25 | 83.33%
|  | 3 | 84 | 0.88 | 1.05
4 lamp | F32T8 | 3 | 89 | 0.96 | 1.08 | 23 | 18 | 78.26%
|  | 4 | 107 | 0.88 | 0.82

## T8 Programmed Start
Source: | http://www.usa.lighting.philips.com/connect/tools_literature/additional-literature/electronic-fluorescent3.wpd
Programmed Start
|  |  | Input power | Ballast Factor | BEF | Using Fixture Input power delta Methodology | Actual Delta | Actual as % of delta watts
0.71 IOP Ballast Factor
1 lamp | F32T8 |  | Not provided
2 lamp | F32T8 | 1 | 26 | 0.73 | 2.81 | #VALUE! | 20 | #VALUE!
|  | 2 | 46 | 0.71 | 1.54
3 lamp | F32T8 | 2 | Not provided |  |  | 25 | #VALUE! | #VALUE!
|  | 3 | 71 | 0.69 | 0.97
4 lamp | F32T8 | 3 | Not provided |  |  | 23 | #VALUE! | #VALUE!
|  | 4 | 94 | 0.71 | 0.76
0.71 GOP Ballast Factor
1 lamp | F32T8 |  | Not provided
2 lamp | F32T8 | 1 | 32 | 0.73 | 2.28 | #VALUE! | 19 | #VALUE!
|  | 2 | 51 | 0.76 | 1.49
3 lamp | F32T8 | 2 | Not provided |  |  | #VALUE! | #VALUE! | #VALUE!
|  | 3 | Not provided
4 lamp | F32T8 | 3 | 80 | 0.74 | 0.93 | #VALUE! | 12 | #VALUE!
|  | 4 | 92 | 0.7 | 0.76
0.88 IOP Ballast Factor
1 lamp | F32T8 |  | Not provided
2 lamp | F32T8 | 1 | 32 | 0.94 | 2.94 | #VALUE! | 26 | #VALUE!
|  | 2 | 58 | 0.85 | 1.47
3 lamp | F32T8 | 2 | Not provided |  |  | 27 | #VALUE! | #VALUE!
|  | 3 | 85 | 0.88 | 1.04
4 lamp | F32T8 | 3 | Not provided |  |  | 25 | #VALUE! | #VALUE!
|  | 4 | 110 | 0.88 | 0.8
0.88 GOP Ballast Factor
1 lamp | F32T8 |  | Not provided
2 lamp | F32T8 | 1 | 34 | 1.03 | 3.03 | #VALUE! | 23 | #VALUE!
|  | 2 | 57 | 0.88 | 1.54
3 lamp | F32T8 | 2 | 66 | 1 | 1.52 | 27 | 18 | 66.67%
|  | 3 | 84 | 0.87 | 1.04
4 lamp | F32T8 | 3 | 93 | 0.93 | 1 | 30 | 21 | 70%
|  | 4 | 114 | 0.88 | 0.77
1.18 IOP Ballast Factor
1 lamp | F32T8 |  | Not provided
2 lamp | F32T8 | 1 | 44 | 1.33 | 3.02 | #VALUE! | 34 | #VALUE!
|  | 2 | 78 | 1.18 | 1.51
3 lamp | F32T8 | 2 | 86 | 1.32 | 1.53 | 32 | 24 | 75%
|  | 3 | 110 | 1.18 | 1.07
4 lamp | F32T8 | 3 | 126 | 1.29 | 1.02 | 43 | 27 | 62.79%
|  | 4 | 153 | 1.18 | 0.77

## Halco
Model Number | NEMA4 Premium® | Voltage (V) | Ballast Type ² | Number of Lamps | Ballast Factor Range | Ballast Factor | Input Watts (W) | BEF³ | Date Added or Modified | Fixture minus Fixture | Delamped | Ballast adjustment | 72.22% | Average
EP232IS/MV/HE | yes | 120/277 | I | 1 | High | 1.08 | 35/34 | 3.09/3.18 | 12/3/2012
EP232IS/120/SL | yes | 120 | I | 1 | High | 1.15 | 38 | 3.0263 | Prior to 9/2012
EP232IS/H/MV/HE | no | 120/277 | I | 1 | High | 1.38 | 45 | 3.07 | 2/1/2013 | 39 | 29 | 74.36%
EP232IS/H/MV/HE | no | 120/277 | I | 2 | High | 1.18 | 74/73 | 1.59/1.62 | 2/1/2013
EP232IS/H/MV/SL | yes | 120/277 | I | 2 | High | 1.18 | 74 | 1.5946 | Prior to 9/2012
EP232IS/L/MV/HE | yes | 277 | I | 2 | Low | 0.78 | 48 | 1.63 | 12/3/2012
EP232IS/MV/HE | yes | 120/277 | I | 2 | Normal | 0.89 | 56/55 | 1.59/1.62 | 12/3/2012
EP232IS/MV/SL | yes | 120/277 | I | 1 | High | 1.15 | 38 | 3.0263 | Prior to 9/2012
EP232PS/L/MV/HE | no | 120/277 | P | 2 | Low | 0.77 | 52/52 | 1.48 | Prior to 9/2012
EP232PS/MV/HE | no | 120/277 | P | 2 | Normal | 0.88 | 60/60 | 1.47 | Prior to 9/2012
EP332IS/H/MV/SL | yes | 120/277 | I | 2 | High | 1.33 | 83 | 1.6024 | Prior to 9/2012
EP332IS/H/MV/SL | yes | 120/277 | I | 3 | High | 1.18 | 108 | 1.09 | Prior to 9/2012
EP332IS/L/MV/HE | yes | 120/277 | I | 2 | Normal | 0.92 | 58/57 | 1.59/1.61 | 1/3/2013 | 26 | 16 | 61.54%
EP332IS/L/MV/HE | yes | 277 | I | 3 | Low | 0.78 | 74 | 1.05 | 1/3/2013
EP332IS/MV/HE | yes | 120/277 | I | 3 | Normal | 0.88 | 84/83 | 1.05/1.06 | 2/1/2013
EP432IS/L/MV/HE | yes | 120/277 | I | 4 | Low | 0.77 | 98/96 | 0.79/0.80 | 10/1/2012
EP432IS/L/MV/SL | yes | 120/277 | I | 3 | Low | 0.84 | 79 | 1.06 | Prior to 9/2012
EP432IS/L/MV/SL | yes | 120/277 | I | 4 | Low | 0.77 | 96 | 0.8 | Prior to 9/2012
EP432IS/MV/HE | yes | 120/277 | I | 3 | Normal | .94/.95 | 89/88 | 1.06/1.08 | Prior to 9/2012 | 26 | 21 | 80.77%
EP432IS/MV/HE | yes | 120/277 | I | 4 | Normal | .88/.87 | 110/106 | .80/.82 | Prior to 9/2012
EP432PS/L/MV/HE | no | 120/277 | P | 3 | Low | .78/.79 | 78 | 1/1.01 | Prior to 9/2012
EP432PS/L/MV/HE | no | 120/277 | P | 4 | Low | 0.74 | 97 | 0.76 | Prior to 9/2012
EP432PS/MV/HE | no | 120/277 | P | 4 | Normal | 0.86 | 114 | 0.75 | Prior to 9/2012
Note on J2: CEE: Ballast factor, input watts, and BEF updated 12/3/2012. On list prior to 9/2012.
Note on J7: CEE: Voltage, ballast factor, input watts, and BEF updated 12/3/2012. Now only meets at 277 volts. On list prior to 12/3/2012 at 120 and 277 volts. Added to list prior to 9/2012.
Note on J8: CEE: Ballast factor, input watts, and BEF updated 12/3/2012. On list prior to 9/2012.
Note on J15: CEE: Ballast factor, input watts, and BEF updated 1/3/2013. Now only meets at 277 volts. On list prior to 1/3/2013 at 120 and 277 volts. Added to list prior to 9/2012.
Note on J16: CEE: Ballast factor, input watts, and BEF updated 2/1/2013. Added to list prior to 9/2012.
Note on J17: CEE: Ballast factor, input watts, and BEF updated. On list prior to 9/2012.

## Universal
B232PUNVHP-A | yes | 120/277 | P | 1 | Normal | 1 | 32 | 3.13 | 6/5/2012 | Fixture minus Fixture | Delamped | Ballast adjustment | 71.61% | Average
B132IUNVEL-A | yes | 120/277 | I | 1 | Low | 0.77 | 25 | 3.08 | 6/5/2012
B132IUNVHE-A | yes | 120/277 | I | 1 | Normal | 0.87 | 28 | 3.11 | 6/5/2012
B132PUNVHP-A | yes | 120/277 | P | 1 | Normal | 0.88 | 31/30 | 2.84/ 2.93 | 6/5/2012
B232I120EL | yes | 120 | I | 2 | Low | 0.77 | 47 | 1.64 | 6/5/2012
B232I120HE | yes | 120 | I | 2 | Normal | 0.87 | 54 | 1.61 | 6/5/2012
B232I2770EL | yes | 277 | I | 2 | Low | 0.77 | 47 | 1.64 | 6/5/2012
B232I277HE | yes | 277 | I | 2 | Normal | 0.87 | 53 | 1.64 | 6/5/2012
B232IUNV104-A | yes | 120/277 | I | 2 | High | 1.04 | 65/64 | 1.60/1.63 | 6/5/2012
B232IUNVEL-A | yes | 120/277 | I | 1 | Normal | 0.95 | 30 | 3.17 | 6/5/2012
B232IUNVEL-A | yes | 120/277 | I | 2 | Low | 0.77 | 48 | 1.6 | 6/5/2012 | 23 | 18 | 78.26%
B232IUNVHE-A | yes | 120/277 | I | 1 | High | 1.05 | 33 | 3.1818 | 6/5/2012
B232IUNVHE-A | yes | 120/277 | I | 2 | Normal | 0.87 | 55 / 54 | 1.58/1.61 | 6/5/2012 | 27 | 22 | 81.48%
B232IUNVHEH-A | yes | 120/277 | I | 2 | High | 1.18 | 74/73 | 1.59/1.61 | 6/5/2012
B232IUNVHP-B | yes | 277 | I | 2 | Normal | 0.88 | 55 | 1.6 | 8/30/2012
B232IUNVHP-N | yes | 120/277 | I | 2 | Normal | 0.88 | 55/53 | 1.60/1.66 | 11/1/2012
B232PUNVEL-A | yes | 120/277 | P | 1 | Low | 0.71 | 25/23 | 2.84/3.09 | 6/5/2012
B232PUNVEL-A | yes | 120/277 | P | 2 | Low | 0.71 | 47/46 | 1.51/1.54 | 6/5/2012
B232PUNVEL-A | yes | 120/277 | P | 2 | Low | 0.71 | 47/46 | 1.51/1.54 | 6/5/2012
B232PUNVEL-B | yes | 120/277 | P | 2 | Low | 0.71 | 46/44 | 1.54/1.61 | 6/5/2012
B232PUNVHE-A | yes | 120/277 | P | 2 | Normal | 0.88 | 56/55 | 1.57/1.60 | 6/5/2012
B232PUNVHE-A | yes | 120/277 | P | 2 | Normal | 0.88 | 56/55 | 1.57/1.60 | 6/5/2012
B232PUNVHE-B | yes | 120/277 | P | 2 | Normal | 0.88 | 55/54 | 1.60/1.63 | 6/5/2012
B232PUNVHEH-A | yes | 120/277 | P | 2 | High | 1.17 | 77/76 | 1.52/1.54 | 2/1/2013
B232PUNVHP-A | yes | 277 | P | 2 | Normal | 0.88 | 60 | 1.47 | 6/5/2012
B332I120EL | yes | 120 | I | 2 | Normal | 0.86 | 53 | 1.62 | 6/5/2012
B332I120EL | yes | 120 | I | 3 | Low | 0.77 | 70 | 1.1 | 6/5/2012 | 23 | 17 | 73.91%
B332I120HE | yes | 120 | I | 2 | Normal | 0.96 | 60 | 1.6 | 6/5/2012
B332I120HE | yes | 120 | I | 3 | Normal | 0.87 | 80 | 1.09 | 6/5/2012 | 26 | 20 | 76.92%
B332I120L-A | yes | 120 | I | 2 | Normal | 0.92 | 58 | 1.59 | 6/5/2012
B332I120RHH | yes | 120 | I | 3 | High | 1.18 | 113 | 1.04 | 6/5/2012
B332I277EL | yes | 277 | I | 2 | Normal | 0.87 | 55 | 1.58 | 6/5/2012
B332I277HE | yes | 277 | I | 2 | High | 1.01 | 61 | 1.66 | 6/5/2012
B332I277HE | yes | 277 | I | 3 | Normal | 0.87 | 79 | 1.1 | 6/5/2012 | 26 | 18 | 69.23%
B332I277RHH | yes | 277 | I | 3 | High | 1.18 | 113 | 1.04 | 6/5/2012
B332I277RHU-A | yes | 277 | I | 3 | High | 1.08 | 102 | 1.06 | 6/5/2012
B332I347HPL | no | 347 | I | 3 | Low | 0.79 | 75 | 1.05 | Prior to 9/2012
B332I347L | no | 347 | I | 3 | Low | 0.79 | 75 | 1.05 | Prior to 9/2012
B332IHRVHB-E | no | 347 | I | 2 | High | 1.22 | 76 | 1.61 | Prior to 9/2012
B332IHRVHB-E | no | 347 | I | 3 | High | 1.18 | 110 | 1.07 | Prior to 9/2012
B332IHRVH-E | no | 347 | I | 3 | High | 1.18 | 110 | 1.07 | Prior to 9/2012
B332IUNVEL-A | yes | 277 | I | 2 | Normal | 0.89 | 56 | 1.59 | 6/5/2012
B332IUNVEL-A | yes | 120/277 | I | 3 | Low | 0.77 | 74 / 73 | 1.04/1.05 | 6/5/2012 | 26 | 18 | 69.23%
B332IUNVHE-A | yes | 120/277 | I | 3 | Normal | 0.87 | 83 / 81 | 1.05/1.07 | 6/5/2012
B332IUNVHEH-A | yes | 120/277 | I | 3 | High | 1.18 | 111/108 | 1.06/1.09 | 6/5/2012
B332IUNVHP-A | yes | 120/277 | I | 3 | Normal | 0.88 | 84/83 | 1.05/1.06 | 10/1/2012
B332PUNVEL-A | yes | 120/277 | P | 3 | Low | 0.71 | 70/69 | 1.01/1.03 | 6/5/2012
B332PUNVHE-A | yes | 120/277 | P | 3 | Normal | 0.88 | 84/82 | 1.05/1.07 | 6/5/2012
B332PUNVHP-A | yes | 120/277 | P | 2 | Normal | 0.99 | 64 / 63 | 1.55/1.57 | 6/5/2012 | 28 | 20 | 71.43%
B423I120HE | yes | 120 | I | 4 | Normal | 0.87 | 106 | 0.82 | 6/5/2012
B432I120EL | yes | 120 | I | 3 | Low | 0.84 | 79 | 1.06 | 6/5/2012
B432I120EL | yes | 120 | I | 4 | Low | 0.77 | 95 | 0.81 | 6/5/2012 | 25 | 16 | 64%
B432I120HE | yes | 120 | I | 3 | Normal | 0.96 | 88 | 1.09 | 6/5/2012
B432I120HE | yes | 120 | I | 4 | Normal | 0.87 | 100 | 0.87 | 6/5/2012 | 20 | 12 | 60%
B432I277EL | yes | 277 | I | 3 | Normal | 0.87 | 76 | 1.14 | 6/5/2012
B432I277EL | yes | 277 | I | 4 | Low | 0.77 | 93 | 0.82 | 6/5/2012
B432I277HE | yes | 277 | I | 3 | Normal | 0.96 | 89 | 1.08 | 6/5/2012
B432I277HE | yes | 277 | I | 4 | Normal | 0.87 | 105 | 0.83 | 6/5/2012
B432I277HEH | yes | 277 | I | 3 | High | 1.28 | 119 | 1.08 | 6/5/2012
B432I277HEH | yes | 277 | I | 4 | High | 1.18 | 145 | 0.81 | 6/5/2012
B432I277L-A | yes | 277 | I | 4 | Low | 0.78 | 98 | 0.8 | 8/30/2012
B432I277RH-A | yes | 277 | I | 4 | Normal | 0.88 | 110 | 0.8 | 6/5/2012
B432I347HP | no | 347 | I | 3 | Normal | 0.99 | 92 | 1.08 | Prior to 9/2012
B432I347HPL | no | 347 | I | 3 | Normal | 0.87 | 83 | 1.05 | Prior to 9/2012
B432IUNV-D | yes | 277 | I | 4 | Normal | 0.88 | 109 | 0.81 | 6/5/2012
B432IUNVEL-A | yes | 120/277 | I | 4 | Low | 0.77 | 97/96 | 0.79/0.80 | 6/5/2012
B432IUNVHE-A | yes | 120/277 | I | 3 | Normal | 0.96 | 84/82 | 1.14/1.17 | 6/5/2012
B432IUNVHE-A | yes | 120/277 | I | 4 | Normal | 0.87 | 109/106 | 0.80/0.82 | 6/5/2012
B432IUNVHP-A | yes | 277 | I | 3 | Normal | 0.94 | 89 | 1.06 | 6/5/2012
B432IUNVHP-A | yes | 120/277 | I | 4 | Normal | 0.88 | 110/108 | 0.80/0.81 | 8/30/2012
B432PUNVEL-A | yes | 120/277 | P | 4 | Low | 0.71 | 91/90 | 0.78/0.79 | Prior to 9/2012
B432PUNVHE-A | yes | 120/277 | P | 4 | Normal | 0.87 | 109/107 | 0.80/0.81 | Prior to 9/2012
B432PUNVHEH-E | yes | 120/277 | P | 3 | High | 1.12 | 103/102 | 1.09/1.10 | 2/1/2013
B432PUNVHEH-E | yes | 120/277 | P | 4 | High | 1.15 | 143/136 | 0.80/0.85 | 2/1/2013
B432PUNVHP-A | yes | 120/277 | P | 3 | Normal | 0.93 | 92/90 | 1.01/1.03 | 6/5/2012
B432PUNVHP-A | yes | 277 | P | 4 | Normal | 0.88 | 115 | 0.77 | 6/5/2012
ES1329A | no | 347 | P | 2 | Normal | 0.87 | 59 | 1.47 | Prior to 9/2012
ES1720B | yes | 120/277 | I | 3 | Normal | 0.87 | 80/82 | 1.09/1.06 | 6/5/2012
ES1720B | yes | 120/277 | I | 4 | Normal | 0.87 | 107/108 | 0.81 | 6/5/2012
Note on J1: CEE: Product name updated to AccuStart8 from F32T8 6/5/2012. On list prior to 6/5/2012.
Note on J2: CEE: Product name updated to Ultim8 from F32T8 6/5/2012. On list prior to 6/5/2012.
Note on J3: CEE: Product name updated to Ultim8 from F32T8 6/5/2012. On list prior to 6/5/2012.
Note on J4: CEE: Product name updated to AccuStart8 from F32T8 6/5/2012. On list prior to 6/5/2012.
Note on J5: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J6: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J7: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J8: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J9: CEE: Product name updated from F32T8 Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J10: CEE: Product name updated to Ultim8 from F32T8 6/5/2012. On list prior to 6/5/2012.
Note on J11: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J12: CEE: Product name updated to Ultim8 from F32T8 6/5/2012. On list prior to 6/5/2012.
Note on J13: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J14: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J15: CEE: Changed to no longer manufactured. On list prior to 8/30/2012. Product name updated to Triad from F32T8 Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J16: CEE: NEMA Premium status updated 11/1/2012. Added to list 8/30/2012.
Note on J17: CEE: Product name updated to Ultim8 from F32T8 6/5/2012. On list prior to 6/5/2012.
Note on J18: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J19: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J20: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J21: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J22: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J23: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J25: CEE: Product name updated from F32T8 Ultim8 to AccuStart8 6/5/2012. On list prior to 6/5/2012.
Note on J26: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J27: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J28: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J29: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J30: CEE: Product name updated from F32 T8 Ultim8 to Triad 6/5/2012. On list prior to 6/5/2012.
Note on J31: CEE: Product name updated from F32 T8 Ultim8 to Triad 6/5/2012. On list prior to 6/5/2012.
Note on J32: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J33: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J34: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J35: CEE: Product name updated from F32 T8 Ultim8 to Triad 6/5/2012. On list prior to 6/5/2012.
Note on J36: CEE: Product name updated from F32 T8 Ultim8 to Triad 6/5/2012. On list prior to 6/5/2012.
Note on J42: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J43: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J44: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J45: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J46: CEE: Input watts and BEF updated 10/1/2012. Now meets at 120 and 277 volts. On list prior to 9/2012 at 277 volts only. Product name updated from F32 T8 Ultim8 to Triad 6/5/2012. On list prior to 6/5/2012 at 277 volts only.
Note on J47: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J48: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J49: CEE: Product name updated from F32T8 Ultim8 to AccuStart8 6/5/2012. On list prior to 6/5/2012.
Note on J50: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J51: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J52: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J53: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J54: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J55: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J56: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J57: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J58: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J59: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J60: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J61: CEE: BEF updated 8/30/2012. Product name updated from F32 T8 to Triad on 6/5/2012. On list prior to 6/5/2012.
Note on J62: CEE: Product name updated from F32 T8 to Triad 6/5/2012. On list prior to 6/5/2012.
Note on J65: CEE: Product name updated from F32 T8 6/5/2012. On list prior to 6/5/2012.
Note on J66: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J67: CEE: Product name updated from F32 T8 Ultim8 to Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J68: CEE: Product name updated 6/5/2012 from F32 T8 to Ultim8. On list prior to 6/5/2012.
Note on J69: CEE: Product name updated from F32 T8 Ultim8 to Triad 6/5/2012. On list prior to 6/5/2012.
Note on J70: CEE: Updated to include 120 volt data 8/30/2012. Product name updated from F32 T8 to Triad 6/5/2012. On list at 277 volts prior to 6/5/2012.
Note on J75: CEE: Product name updated from F32 T8 Ultim8 to AccuStart8 6/5/2012. On list prior to 6/5/2012.
Note on J76: CEE: Product name updated from F32 T8 to AccuStart8 6/5/2012. On list prior to 6/5/2012.
Note on J78: CEE: Product name updated from F32 T8 Ultim8 6/5/2012. On list prior to 6/5/2012.
Note on J79: CEE: Product name updated from F32 T8 6/5/2012. On list prior to 6/5/2012.